## Calculator
Z "Tooth" Compressor Element Calculator
| ZT22 | Model
Low Pressure Element
| 0 | Altitude of facility location
| Loaded | PSIG | Intake Gauge Pressure
| -7 | PSIG | intercooler reading, from the Electronicon (26 -35 normal upto 56)
unloaded you should see -6 to -9
High Pressure Element
| 105 | PSIG | discharge gauge pressure, from electronicon
Low Pressure Element Compression Ratio: 0.6
| 29.92 | InHg - Barometric Pressure |  | -1 | PSIG - Intake Gauge Pressure |  |  | -7 | PSIG - Discharge Gauge Pressure
| 0.4912 | Atmospheric Press conv factor |  | 13.6967 | PSIA - Intake Pressure Absolute |  |  | 7.6967 | PSIA - Discharge Pressure Absolute
| 14.6967 | PSIA - Atmospheric Pressure
High Pressure Element Compression Ratio: 15.6
| 29.92 | InHg - Barometric Pressure |  | -7 | PSIG - Intake Gauge Pressure |  |  | 105 | PSIG - Discharge Gauge Pressure
| 0.4912 | Atmospheric Press conv factor |  | 7.6967 | PSIA - Intake Pressure Absolute |  |  | 119.6967 | PSIA - Discharge Pressure Absolute
| 14.6967 | PSIA - Atmospheric Pressure
| 73 | Inlet Air Temperature F
| 85 | Intercooler Discharge Temperature F
Low Pressure Element Discharge Temperature: -21.9
| 73 | ° F - Element Inlet Temp (T1) |  |  | 13.6967 | PSIA - Intake Pressure Absolute |  |  |  | 0.82204 | (Po/Pi)SF
| 533 | ° R - Element Inlet Temp |  |  | 0.56194 | Pressure Ratio
| 7.6967 | PSIA - Discharge Pressure Absolute (Po) |  |  | 0.34 | Element Concersion Factor
High Pressure Element Discharge Temperature: 964
| 85 | ° F - Element Inlet Temp (T1) |  |  | 7.6967 | PSIA - Intake Pressure Absolute (Pi) |  |  |  | 2.6129 | (Po/Pi)SF
| 545 | ° R - Element Inlet Temp |  |  | 15.5517 | Pressure Ratio
| 119.6967 | PSIA - Discharge Pressure Absolute (Po) |  |  | 0.35 | Element Concersion Factor
[7 empty] | T2 | Theoretical Discharge Temp
|  | Theoretical Discharge Temp Calculation |  |  |  |  | T1 | Element Inlet temp in Rankine
|  | T2 = [(T1)(P0/Pi)SF]-460 |  |  |  |  | Po | Element Outlet pressure in PSIA
[7 empty] | Pi | Element Inlet Pressure in PSIA
[7 empty] | SF | 0.34 LP Element / 0.35 HP Element
[7 empty] | R | 460

## Data
Tooth Element Stage Factors |  |  | LP Element Compression Ratio
| Stage | Air Cooled | 0.56194 | /
LP | Low Press Element | 0.34 | HP Element Compression Ratio
HP | High Press Element | 0.35 | 15.5517 | /
|  |  | Low Pressure Element Intake Pressure |  |  | 0.34 | 0.35
0 | 29.92 | 14.7 | Loaded | -1 | Model | LP fac | HP fac
250 | 29.65 | 14.56 | Unloaded | -13 | ZT18 | 0.34 | 0.35
500 | 29.38 | 14.43 |  |  | ZT22 | 0.34 | 0.35
750 | 29.12 | 14.3 |  |  | ZT30 | 0.34 | 0.35
1000 | 28.86 | 14.16 |  |  | ZT237 | 0.33 | 0.34
1250 | 28.6 | 14.05 |  |  | ZT37 | 0.33 | 0.34
1500 | 28.33 | 13.91 |  |  | ZT245 | 0.33 | 0.34
1750 | 28.08 | 13.79 |  |  | ZT45 | 0.33 | 0.34
2000 | 27.82 | 13.66 |  |  | ZT255 | 0.33 | 0.34
2250 | 27.57 | 13.54 |  |  | ZT55 | 0.33 | 0.34
2500 | 27.32 | 13.41 |  |  | ZT275 | 0.33 | 0.34
2750 | 27.07 | 13.3 |  |  | ZT75 | 0.33 | 0.335
3000 | 26.82 | 13.17 |  |  | ZT290 | 0.33 | 0.34
3250 | 26.58 | 13.05 |  |  | ZT90 | 0.33 | 0.335
3500 | 26.33 | 12.93 |  |  | ZR237 | 0.33 | 0.34
3750 | 26.09 | 12.81 |  |  | ZR37 | 0.33 | 0.34
4000 | 25.84 | 12.69 |  |  | ZR245 | 0.33 | 0.34
4250 | 25.61 | 12.58 |  |  | ZR45 | 0.33 | 0.34
4500 | 25.37 | 12.46 |  |  | ZR255 | 0.33 | 0.34
4750 | 25.14 | 12.35 |  |  | ZR55 | 0.33 | 0.34
5000 | 24.9 | 12.23 |  |  | ZR275 | 0.33 | 0.34
5250 | 24.67 | 12.12 |  |  | ZR75 | 0.33 | 0.335
5500 | 24.44 | 12 |  |  | ZR290 | 0.33 | 0.34
5750 | 24.21 | 11.89 |  |  | ZR90 | 0.33 | 0.335
6000 | 23.99 | 11.78 |  |  | ZA3 | 0.33 | N/A
[5 empty] | ZA4 | 0.325 | N/A
[5 empty] | ZA5 | 0.32 | N/A
[5 empty] | ZA6 | 0.32 | N/A
[5 empty] | ZR3 | 0.33 | 0.335
[5 empty] | ZR4 | 0.325 | 0.33
[5 empty] | ZR5 | 0.32 | 0.33
[5 empty] | ZR6 | 0.32 | 0.325
[5 empty] | ZT3 | 0.345 | 0.35
[5 empty] | ZT4 | 0.34 | 0.345