Medical Gas Permit-to-Work

| GENERAL |  |  |  |
| --- | --- | --- | --- |
| Healthcare Facility Name: | Lewis Medical Center | City/ST: | Ronks, PA |
| Brief Summary of Work: | Shutting off oxygen zone valve adjacent to ED Room 25 in order to replace oxygen rough-ins located in ED Room 31. |  |  |
| Permit Number: | J0909 | Date of Issue: | 1/16/25 |
| Work Order Number: | WO11625 | Expires: | 2/16/25 |

| Building: | East Tower, Heart Center, etc. |  |  | Floor: |  | 1st Floor, 2nd Floor, etc. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Unit(s) Affected: | 3100, ICU, Radiology, Endo, etc. |  |  | Room(s) Affected: |  | 3101, ED Room 25, NICU Bed 1, etc. |  |
| Gas(es) affected: | ▢ Medical Oxygen ▢ Medical Vacuum ▢ Medical Air ▢ WAGD ▢ Nitrous Oxide ▢ Nitrogen ▢ Carbon Dioxide ▢ Instrument Air ▢ Other ______________________________________ |  |  |  |  |  |  |
| Type of Work: | ▢ Preventative/Predictive Maintenance ▢ Failure Repair ▢ New Construction ▢ Other____________________________________________________________________________ |  |  |  |  |  |  |
| Project Date: | 3/14/25 | Start Time: | 6:00am |  | End Time (estimated): |  | 10:00am |

DETAILED SCOPE

Shutting off oxygen zone valve outside ED Room 25. Oxygen supply to ED rooms 21-40 will be disrupted for approximately 2 hours. Inline valves above ceiling in ED hallway will remain open. Oxygen H-cylinder backfeed setup to be located in ED 29. Backfeeds will be monitored by respiratory therapy and medical gas verifier. Repairs expected to take approximately one hour, medical gas verification another hour.

| RISK ASSESSMENT & CHECKLIST |  |
| --- | --- |
| Room/Area Risk Category: | ▢ Category 1 (failure could cause major injury or death) ▢ Category 2 (failure could cause minor injury) ▢ Category 3 (failure could cause discomfort or inconvenience) |
| Pre-Work Checklist: | ▢ Clinical impact assessed and communicated to affected department(s). ▢ Shutdown window communicated to staff. ▢ All appropriate authorizations received for High Hazard work. ▢ Temporary medical gas supply arranged (D/E/H cylinders, portable suction pumps, etc.). ▢ Carts, straps, and stands available to transport and secure cylinders used for temporary supply. ▢ Only qualified staff will operate and monitor cylinders used for temporary supply. ▢ If work involves medical gas alarm panels, ILSM is in place for duration of alarm outage. ▢ Required testing and verification planned. ▢ Work area isolated/protected. ▢ ICRA/PCRA checklists completed. |
| Project Hazard Type: | ▢ Low Hazard ( planned maintenance, basic repairs, work in Category 3 areas, etc.*) ▢ High Hazard (shutdowns involving gas supplying Category 1 areas, system replacements, new work requiring 6030 Verification, etc.*) *These are illustrative examples only and do not reflect the full extent of medical gas projects that carry significant inherit risk. Classifications such as these should be done by a qualified individual or team, reviewed and approved by the local Authority Having Jurisdiction and incorporated into each facility’s policies and procedures. |
| Specific Potential Risks: | ▢ System Contamination ▢ Cross-Connection ▢ Pressure Loss/Supply Interruption ▢ Monitoring Interruption ▢ Other____________________________________________________________________ |

EOP RECOMMENDATION

A review of the facility’s Medical Gas Emergency Operations Plan is recommended before any High-Hazard work or any projects requiring gas outages.

PERSONNEL

| RESPONSIBLE FACILITY AUTHORITY |  |
| --- | --- |
| RFA Name: |  |
| Phone: |  |
| Email: |  |
| Qualification: |  |

| ALL WORK |  |  |  |
| --- | --- | --- | --- |
| Medical Gas Technician: |  |  |  |
| Phone: |  |  |  |
| Qualification: | ▢ A documented and equipment-specific training program acceptable to facility ~ 5.1.14.4.2.5(B)(1) ▢ ASSE/IAPMO/ANSI 6040 ~ 5.1.14.4.2.5(B)(2) ▢ ASSE/IAPMO/ANSI 6030 ~ 5.1.14.4.2.5(B)(3) |  |  |
| Engineering Supervisor: |  | Phone: |  |

| HIGH HAZARD ONLY (not all may be applicable to every job) |  |  |  |
| --- | --- | --- | --- |
| Director/Executive Contact: |  | Phone: |  |
| Medical Gas Verifier: |  |  |  |
| Verifier Phone Number: |  | Credentials: |  |
| Clinical Contact: |  | Phone: |  |
| Respiratory Therapy Contact: |  | Phone: |  |
| Safety Officer Contact: |  | Phone: |  |
| Infection Control: |  | Phone: |  |
| General Contractor: |  | Phone: |  |
| Mechanical Contractor: |  | Phone: |  |

| RECORD OF MEDICAL GAS VALVE CLOSURE |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Valve Type: | ▢ Source ▢ Riser ▢ Service ▢ Inline ▢ Zone | Valve Location: |  | Area Served: |  | Date Closed: Time Closed: Time Open: Initials: |  |
| Valve Type: | ▢ Source ▢ Riser ▢ Service ▢ Inline ▢ Zone | Valve Location: |  | Area Served: |  | Date Closed: Time Closed: Time Open: Initials: |  |
| Valve Type: | ▢ Source ▢ Riser ▢ Service ▢ Inline ▢ Zone | Valve Location: |  | Area Served: |  | Date Closed: Time Closed: Time Open: Initials: |  |
| Valve Type: | ▢ Source ▢ Riser ▢ Service ▢ Inline ▢ Zone | Valve Location: |  | Area Served: |  | Date Closed: Time Closed: Time Open: Initials: |  |

| JOB COMPLETION |  |
| --- | --- |
| Date of Completion: |  |
| Status: | ▢ All Work Complete ▢ Work Complete w/ exception(s) |
| Follow-Up / Exception(s): |  |
| Post-Work Checklist: | ▢ Visual inspection of in-wall piping integrity and 24-hr standing pressure test completed and documented (if required). ▢ Medical gas verification complete (if required). ▢ Any valves closed during work have been re-opened and all gases are back online. ▢ Clinical staff and relevant department heads have been notified that work is complete and any interrupted services have been fully restored. ▢ Any valves added or modified during new work have been labeled accurately with valve type, gas type, and specific area served. ▢ All area alarm and zone valve labels have been updated to reflect changes resulting from medical gas outlets being added to or removed from patients rooms. |

| FINAL SIGN-OFF |  |
| --- | --- |
| Medical Gas Technician: |  |
| Signature: |  |
| RFA (if applicable): |  |
| Signature: |  |
| Engineering Supervisor: |  |
| Signature: |  |

Before initiating work on medical gas systems, ensure precautions are in place as required by NFPA 99 Health Care Facilities Code and ASSE/IAPMO/ANSI Series 6000 Professional Qualifications Standard for Medical Gas Systems Personnel. This Permit to Work is required for any operation involving medical gas and vacuum systems. This work includes, but is not limited to, installation, maintenance, testing, repair, modification, or decommissioning of any part of a medical gas system. This document is intended to comply with all requirements of the NFPA 99, ASSE 6000 and other applicable codes and standards. By using this document, you agree to hold harmless and indemnify Lantern Medical, LLC from any and all claims, damages, losses, and expenses, including legal fees, arising out of or resulting from your use or misuse of this document.

www.lanternacademy.com